## Slide 1: Treatment –Reverse Osmosis (Desalination)
DWQR Risk Assessment Training
2018

## Slide 2: Overview
Not that common
Not a cheap option
Osmosis – water passes from weaker solution to more concentrated
Can be made to flow in opposite direction (RO) across membrane by applying pressure
Produces almost pure water plus concentrated waste stream
OTT for most PWS but OK for difficult to treat situations
Removes almost everything from water
MUST have pre-treatment and Remineralisation
Can be point of use
Significant purchase and running cost

## Slide 3: Usage 1
Situations where nothing else will work
Often mineral / chemical contamination ( As, B, Pb, Cd, Cr, Cu, Sb )
Also removes pathogens – providing there is no re-contamination
Should remove colour-causing organic compounds

## Slide 4: Usage 2
Several stages of pre-treatment needed to prevent RO fouling
Pre-treatment filters often built into unit. Are they sufficient?
Water CANNOT be drunk straight from RO – must be remineralised
RO water is corrosive to pipework (and humans!)
Membranes may be cleaned (for PWS usually replaced – running cost)

## Slide 5: Key Points to Watch For
May be installed as an “over the top” solution by inexperienced engineers
How do you know the membrane has not been breached? (monitor for contaminant)
If flow dropping, membrane may be fouling or scaling
Maintenance programme for replacement of filters & re-mineralisation
Are all taps in property covered (often “under sink solution”)
Is the concentrate being disposed of properly?

## Slide 6: Questions
Hazard Type | Location | Risk No. | Potential Risk | Explanation of Hazard | Severity
Installation and Operation | Treatment | TRO1 | Is RO (Reverse Osmosis) plant specification/ design inadequate for raw water quality? | The water quality challenges should be clearly understood and the membrane selected should be appropriate to water quality in a range of conditions. | 5
Installation and Operation | Treatment | TRO2 | Could pre-treatment be inadequate, resulting in RO fouling and damage (such as inadequate removal of oxidants)? | RO membranes require clean water at the inlet. In almost all cases comprehensive pre-treatment will be required to ensure water meets the specification. Inadequate pre-treatment will result in fouling of the membrane and, potentially, lasting damage. | 4
Installation and Operation | Treatment | TRO3 | Is there a risk from inadequate re-mineralisation of the water following RO? | Re-mineralisation is vital after RO as the water has been stripped of minerals and is very corrosive. This step should be incorporated in plant design and any equipment maintained in accordance with the manufacturer's specifications. | 3
Management and Management and Resilience | Treatment | TRO4 | Are the cleaning regimes (for descaling and antifouling, etc.) inadequate or undocumented? | Membranes require a specific cleaning regime at regular intervals. Care should be taken that the manufacturer's specifications are followed and the correct procedures and chemicals used. | 5
Management and Management and Resilience | Treatment | TRO5 | Are the chemicals used in the process incorrect or stored incorrectly? | Many membrane cleaning chemicals are acids or alkalis and require specific storage conditions to ensure that they remain effective and are in a safe condition. | 4
Installation and Operation | Treatment | TRO6 | Could a loss of membrane integrity go undetected? | If the membrane is breached it will not provide a reliable barrier. How would this be picked up? Some membranes have integral automatic detection systems, but other systems may rely on monitoring or sampling. The appropriate integrity monitoring system will depend on the type of membrane and water quality - specialist advice should be sought. | 5
Installation and Operation | Treatment | TR07 | Could failures occur due to membranes not being replaced as per the manufacturer's specifications? | The manufacturer will specify the frequency at which the filters should be replaced. Ask for evidence that this is being adhered to. Membrane elements need to be handled with care and manufacturers' specifications should be followed closely. | 5